## Tank Master
SAPID | Location | Device Name | Tank ID | Tank Type | Product | ESD Active | Normal value | Primary Gauge Level | Normal value | Sensor_Id | Sensor_Type | Tank Receipt Mode | Normal value | TANK LEAKAGE STATUS | Normal value | Primary Gauge HIGH | Normal Value | Sensor_Id | Sensor_Type | Primary Gauge HIGH HIGH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF OK | Normal Value | Sensor_Id | Sensor_Type | LEVEL SWITCH PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | RADAR HHH | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF OK | Normal Value | Sensor_Id | Sensor_Type | RADAR PROOF FAILED | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL1 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS IL2 | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS OL | Normal value | Sensor_Id | Sensor_Type | ROSOV OPEN STATUS RCL | Normal value | Sensor_Id | Sensor_Type | ROSOV FAIL TO CLOSE STATUS RCL | Normal value | Sensor_Id | Sensor_Type | MOV STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV STATUS OL | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS OL |  | Sensor_Id | Sensor_Type | MOV STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | MOV REMOTE STATUS RCL | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FIRE ALARM | Normal Value | Sensor_Id | Sensor_Type | RIMSEAL FAULT ALARM | Normal Value | Sensor_Id | Sensor_Type
1636 | Balasore | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-01.LEVEL |  | TK-01 | Primary Radar |  |  | TANK.TK-01.TANK_ALERT_ALARM | 0 | TANK.TK-01.HIGH_LEVEL | 0 | TK-01 | Primary Radar | TANK.TK-01.HIGH_HIGH_LEVEL | 0 | TK-01 | Primary Radar | LEVELSWITCH.LSW-01.SWITCH_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_OK | 0 | LSW-01 | VFT | LEVELSWITCH.LSW-01.PROOF_TEST_FAILED | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.SWITCH_STATUS | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_OK | 0 | RDR-01 | RADAR | LEVELSWITCH.RDR-01.PROOF_TEST_FAILED | 0 | RDR-01 | RADAR | MOV.ROSOV-03.OPEN_STATUS | 0 | ROSOV-03 | ROSOV IL1 | MOV.ROSOV-03.FAILED_TO_CLOSE | 0 | ROSOV-03 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-02.OPEN_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-02.FAILED_TO_CLOSE | 0 | ROSOV-02 | ROSOV FAILED OL | MOV.ROSOV-01.OPEN_STATUS | 0 | ROSOV-01 | ROSOV RCL | MOV.ROSOV-01.FAILED_TO_CLOSE | 0 | ROSOV-01 | ROSOV FAILED RCL | MOV.MOV-03.OPEN_STATUS | 0 | MOV-03 | MOV IL1 | MOV.MOV-03.REMOTE_STATUS | 1 | MOV-03 | MOV IL1 |  |  |  |  | MOV.MOV-01.OPEN_STATUS | 0 | MOV-01 | MOV OL | MOV.MOV-01.REMOTE_STATUS | 1 | MOV-01 | MOV OL | MOV.MOV-02.OPEN_STATUS | 0 | MOV-02 | MOV RCL | MOV.MOV-02.REMOTE_STATUS | 1 | MOV-02 | MOV RCL
1636 | Balasore | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-02.LEVEL |  | TK-02 | Primary Radar |  |  | TANK.TK-02.TANK_ALERT_ALARM | 0 | TANK.TK-02.HIGH_LEVEL | 0 | TK-02 | Primary Radar | TANK.TK-02.HIGH_HIGH_LEVEL | 0 | TK-02 | Primary Radar | LEVELSWITCH.LSW-02.SWITCH_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_OK | 0 | LSW-02 | VFT | LEVELSWITCH.LSW-02.PROOF_TEST_FAILED | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.SWITCH_STATUS | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_OK | 0 | RDR-02 | RADAR | LEVELSWITCH.RDR-02.PROOF_TEST_FAILED | 0 | RDR-02 | RADAR | MOV.ROSOV-06.OPEN_STATUS | 0 | ROSOV-06 | ROSOV IL1 | MOV.ROSOV-06.FAILED_TO_CLOSE | 0 | ROSOV-06 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-05.OPEN_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-05.FAILED_TO_CLOSE | 0 | ROSOV-05 | ROSOV FAILED OL | MOV.ROSOV-04.OPEN_STATUS | 0 | ROSOV-04 | ROSOV RCL | MOV.ROSOV-04.FAILED_TO_CLOSE | 0 | ROSOV-04 | ROSOV FAILED RCL | MOV.MOV-04.OPEN_STATUS | 0 | MOV-04 | MOV IL1 | MOV.MOV-04.REMOTE_STATUS | 1 | MOV-04 | MOV IL1 |  |  |  |  | MOV.MOV-05.OPEN_STATUS | 0 | MOV-05 | MOV OL | MOV.MOV-05.REMOTE_STATUS | 1 | MOV-05 | MOV OL | MOV.MOV-06.OPEN_STATUS | 0 | MOV-06 | MOV RCL | MOV.MOV-06.REMOTE_STATUS | 1 | MOV-06 | MOV RCL
1636 | Balasore | TK-03_SKO | TK-03 | AG | SKO | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-03.LEVEL |  | TK-03 | Primary Radar |  |  | TANK.TK-03.TANK_ALERT_ALARM | 0 | TANK.TK-03.HIGH_LEVEL | 0 | TK-03 | Primary Radar | TANK.TK-03.HIGH_HIGH_LEVEL | 0 | TK-03 | Primary Radar | LEVELSWITCH.LSW-03.SWITCH_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_OK | 0 | LSW-03 | VFT | LEVELSWITCH.LSW-03.PROOF_TEST_FAILED | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.SWITCH_STATUS | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_OK | 0 | RDR-03 | RADAR | LEVELSWITCH.RDR-03.PROOF_TEST_FAILED | 0 | RDR-03 | RADAR | MOV.ROSOV-09.OPEN_STATUS | 0 | ROSOV-09 | ROSOV IL1 | MOV.ROSOV-09.FAILED_TO_CLOSE | 0 | ROSOV-09 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-08.OPEN_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-08.FAILED_TO_CLOSE | 0 | ROSOV-08 | ROSOV FAILED OL | MOV.ROSOV-07.OPEN_STATUS | 0 | ROSOV-07 | ROSOV RCL | MOV.ROSOV-07.FAILED_TO_CLOSE | 0 | ROSOV-07 | ROSOV FAILED RCL | MOV.MOV-09.OPEN_STATUS | 0 | MOV-09 | MOV IL1 | MOV.MOV-09.REMOTE_STATUS | 1 | MOV-09 | MOV IL1 |  |  |  |  | MOV.MOV-08.OPEN_STATUS | 0 | MOV-08 | MOV OL | MOV.MOV-08.REMOTE_STATUS | 1 | MOV-08 | MOV OL | MOV.MOV-07.OPEN_STATUS | 0 | MOV-07 | MOV RCL | MOV.MOV-07.REMOTE_STATUS | 1 | MOV-07 | MOV RCL
1636 | Balasore | TK-04_ETHANOL | TK-04 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-04.LEVEL |  | TK-04 | Primary Radar |  |  | TANK.TK-04.TANK_ALERT_ALARM | 0 | TANK.TK-04.HIGH_LEVEL | 0 | TK-04 | Primary Radar | TANK.TK-04.HIGH_HIGH_LEVEL | 0 | TK-04 | Primary Radar | LEVELSWITCH.LSW-04.SWITCH_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_OK | 0 | LSW-04 | VFT | LEVELSWITCH.LSW-04.PROOF_TEST_FAILED | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.SWITCH_STATUS | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_OK | 0 | RDR-04 | RADAR | LEVELSWITCH.RDR-04.PROOF_TEST_FAILED | 0 | RDR-04 | RADAR | MOV.ROSOV-12.OPEN_STATUS | 0 | ROSOV-12 | ROSOV IL1 | MOV.ROSOV-12.FAILED_TO_CLOSE | 0 | ROSOV-12 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-11.OPEN_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-11.FAILED_TO_CLOSE | 0 | ROSOV-11 | ROSOV FAILED OL | MOV.ROSOV-10.OPEN_STATUS | 0 | ROSOV-10 | ROSOV RCL | MOV.ROSOV-10.FAILED_TO_CLOSE | 0 | ROSOV-10 | ROSOV FAILED RCL | MOV.MOV-12.OPEN_STATUS | 0 | MOV-12 | MOV IL1 | MOV.MOV-12.REMOTE_STATUS | 1 | MOV-12 | MOV IL1 |  |  |  |  | MOV.MOV-11.OPEN_STATUS | 0 | MOV-11 | MOV OL | MOV.MOV-11.REMOTE_STATUS | 1 | MOV-11 | MOV OL | MOV.MOV-10.OPEN_STATUS | 0 | MOV-10 | MOV RCL | MOV.MOV-10.REMOTE_STATUS | 1 | MOV-10 | MOV RCL
1636 | Balasore | TK-05_BS VI MS | TK-05 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-05.LEVEL |  | TK-05 | Primary Radar |  |  | TANK.TK-05.TANK_ALERT_ALARM | 0 | TANK.TK-05.HIGH_LEVEL | 0 | TK-05 | Primary Radar | TANK.TK-05.HIGH_HIGH_LEVEL | 0 | TK-05 | Primary Radar | LEVELSWITCH.LSW-05.SWITCH_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_OK | 0 | LSW-05 | VFT | LEVELSWITCH.LSW-05.PROOF_TEST_FAILED | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.SWITCH_STATUS | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_OK | 0 | RDR-05 | RADAR | LEVELSWITCH.RDR-05.PROOF_TEST_FAILED | 0 | RDR-05 | RADAR | MOV.ROSOV-15.OPEN_STATUS | 0 | ROSOV-15 | ROSOV IL1 | MOV.ROSOV-15.FAILED_TO_CLOSE | 0 | ROSOV-15 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-13.OPEN_STATUS | 0 | ROSOV-13 | ROSOV OL | MOV.ROSOV-13.FAILED_TO_CLOSE | 0 | ROSOV-13 | ROSOV FAILED OL | MOV.ROSOV-14.OPEN_STATUS | 0 | ROSOV-14 | ROSOV RCL | MOV.ROSOV-14.FAILED_TO_CLOSE | 0 | ROSOV-14 | ROSOV FAILED RCL | MOV.MOV-15.OPEN_STATUS | 0 | MOV-15 | MOV IL1 | MOV.MOV-15.REMOTE_STATUS | 1 | MOV-15 | MOV IL1 |  |  |  |  | MOV.MOV-13.OPEN_STATUS | 0 | MOV-13 | MOV OL | MOV.MOV-13.REMOTE_STATUS | 1 | MOV-13 | MOV OL | MOV.MOV-14.OPEN_STATUS | 0 | MOV-14 | MOV RCL | MOV.MOV-14.REMOTE_STATUS | 1 | MOV-14 | MOV RCL
1636 | Balasore | TK-07_BS VI MS | TK-07 | AG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-07.LEVEL |  | TK-07 | Primary Radar |  |  | TANK.TK-07.TANK_ALERT_ALARM | 0 | [8 empty] | LEVELSWITCH.LSW-07.SWITCH_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_OK | 0 | LSW-07 | VFT | LEVELSWITCH.LSW-07.PROOF_TEST_FAILED | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.SWITCH_STATUS | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_OK | 0 | RDR-07 | RADAR | LEVELSWITCH.RDR-07.PROOF_TEST_FAILED | 0 | RDR-07 | RADAR | MOV.ROSOV-16.OPEN_STATUS | 0 | ROSOV-16 | ROSOV IL1 | MOV.ROSOV-16.FAILED_TO_CLOSE | 0 | ROSOV-16 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-17.OPEN_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-17.FAILED_TO_CLOSE | 0 | ROSOV-17 | ROSOV FAILED OL | MOV.ROSOV-18.OPEN_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.ROSOV-18.FAILED_TO_CLOSE | 0 | ROSOV-18 | ROSOV FAILED RCL | MOV.MOV-16.OPEN_STATUS | 0 | MOV-16 | MOV IL1 | MOV.MOV-16.REMOTE_STATUS | 1 | MOV-16 | MOV IL1 |  |  |  |  | MOV.MOV-17.OPEN_STATUS | 0 | MOV-17 | MOV OL | MOV.MOV-17.REMOTE_STATUS | 1 | MOV-17 | MOV OL | MOV.MOV-18.OPEN_STATUS | 0 | MOV-18 | MOV RCL | MOV.MOV-18.REMOTE_STATUS | 1 | MOV-18 | MOV RCL
1636 | Balasore | TK-08_BS VI MS | TK-08 | UG | BS VI MS | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-08.LEVEL |  | TK-08 | Primary Radar |  |  | TANK.TK-08.TANK_ALERT_ALARM | 0 | TANK.TK-08.HIGH_LEVEL | 0 | TK-08 | Primary Radar | TANK.TK-08.HIGH_HIGH_LEVEL | 0 | TK-08 | Primary Radar
1636 | Balasore | TK-09_ETHANOL | TK-09 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-09.LEVEL |  | TK-09 | Primary Radar |  |  | TANK.TK-09.TANK_ALERT_ALARM | 0 | TANK.TK-09.HIGH_LEVEL | 0 | TK-09 | Primary Radar | TANK.TK-09.HIGH_HIGH_LEVEL | 0 | TK-09 | Primary Radar
1636 | Balasore | TK-10_BS VI HSD | TK-10 | UG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-10.LEVEL |  | TK-10 | Primary Radar |  |  | TANK.TK-10.TANK_ALERT_ALARM | 0 | TANK.TK-10.HIGH_LEVEL | 0 | TK-10 | Primary Radar | TANK.TK-10.HIGH_HIGH_LEVEL | 0 | TK-10 | Primary Radar
1636 | Balasore | TK-11_WATER | TK-11 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-11.LEVEL |  | TK-11 | Primary Radar |  |  | TANK.TK-11.TANK_ALERT_ALARM | 0 | TANK.TK-11.HIGH_LEVEL | 0 | TK-11 | Primary Radar | TANK.TK-11.HIGH_HIGH_LEVEL | 0 | TK-11 | Primary Radar
1636 | Balasore | TK-12_WATER | TK-12 | AG | WATER | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-12.LEVEL |  | TK-12 | Primary Radar |  |  | TANK.TK-12.TANK_ALERT_ALARM | 0 | TANK.TK-12.HIGH_LEVEL | 0 | TK-12 | Primary Radar | TANK.TK-12.HIGH_HIGH_LEVEL | 0 | TK-12 | Primary Radar
1636 | Balasore | TK-13_BS VI HSD | TK-13 | AG | BS VI HSD | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-13.LEVEL |  | TK-13 | Primary Radar |  |  | TANK.TK-13.TANK_ALERT_ALARM | 0 | TANK.TK-13.HIGH_LEVEL | 0 | TK-13 | Primary Radar | TANK.TK-13.HIGH_HIGH_LEVEL | 0 | TK-13 | Primary Radar
1636 | Balasore | TK-14_ETHANOL | TK-14 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-14.LEVEL |  | TK-14 | Primary Radar |  |  | TANK.TK-14.TANK_ALERT_ALARM | 0 | TANK.TK-14.HIGH_LEVEL | 0 | TK-14 | Primary Radar | TANK.TK-14.HIGH_HIGH_LEVEL | 0 | TK-14 | Primary Radar
1636 | Balasore | TK-15_ETHANOL | TK-15 | AG | ETHANOL | PLC.SFTPLC.ANY_ESD_PB_ACTI | 0 | TANK.TK-15.LEVEL |  | TK-15 | Primary Radar |  |  | TANK.TK-15.TANK_ALERT_ALARM | 0 | TANK.TK-15.HIGH_LEVEL | 0 | TK-15 | Primary Radar | TANK.TK-15.HIGH_HIGH_LEVEL | 0 | TK-15 | Primary Radar | LEVELSWITCH.LSW-06.SWITCH_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_OK | 0 | LSW-06 | VFT | LEVELSWITCH.LSW-06.PROOF_TEST_FAILED | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.SWITCH_STATUS | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_OK | 0 | RDR-06 | RADAR | LEVELSWITCH.RDR-06.PROOF_TEST_FAILED | 0 | RDR-06 | RADAR | MOV.ROSOV-19.OPEN_STATUS | 0 | ROSOV-19 | ROSOV IL1 | MOV.ROSOV-19.FAILED_TO_CLOSE | 0 | ROSOV-19 | ROSOV FAILED IL1 | [8 empty] | MOV.ROSOV-20.OPEN_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-20.FAILED_TO_CLOSE | 0 | ROSOV-20 | ROSOV FAILED OL | MOV.ROSOV-21.OPEN_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.ROSOV-21.FAILED_TO_CLOSE | 0 | ROSOV-21 | ROSOV FAILED RCL | MOV.MOV-19.OPEN_STATUS | 0 | MOV-19 | MOV IL1 | MOV.MOV-19.REMOTE_STATUS | 1 | MOV-19 | MOV IL1 |  |  |  |  | MOV.MOV-20.OPEN_STATUS | 0 | MOV-20 | MOV OL | MOV.MOV-20.REMOTE_STATUS | 1 | MOV-20 | MOV OL | MOV.MOV-21.OPEN_STATUS | 0 | MOV-21 | MOV RCL | MOV.MOV-21.REMOTE_STATUS | 1 | MOV-21 | MOV RCL

## HDR Line MOV
SAPID | Location | Device Name | Product | MOV ID | HDR MOV STATUS | Normal Value | HDR MOV REMOTE STATUS | Normal Value | HDR MOV MAINTENANCE STATUS | Normal Value
1636 | Balasore | TOBV-01_HDR-TOBV-MS | HDR-TOBV-MS | TOBV-01 | MOV.TOBV-01.OPEN_STATUS | TRUE | MOV.TOBV-01.REMOTE_STATUS | TRUE | MOV.TOBV-01.MAINTENANCE_STATUS | FALSE
1636 | Balasore | TOBV-02_HDR-TOBV-HSD | HDR-TOBV-HSD | TOBV-02 | MOV.TOBV-02.OPEN_STATUS | TRUE | MOV.TOBV-02.REMOTE_STATUS | TRUE | MOV.TOBV-02.MAINTENANCE_STATUS | FALSE
1636 | Balasore | TOBV-03_HDR-TOBV-SKO | HDR-TOBV-SKO | TOBV-03 | MOV.TOBV-03.OPEN_STATUS | TRUE | MOV.TOBV-03.REMOTE_STATUS | TRUE | MOV.TOBV-03.MAINTENANCE_STATUS | FALSE
1636 | Balasore | TOBV-04_HDR-TOBV-ETH | HDR-TOBV-ETH | TOBV-04 | MOV.TOBV-04.OPEN_STATUS | TRUE | MOV.TOBV-04.REMOTE_STATUS | TRUE | MOV.TOBV-04.MAINTENANCE_STATUS | FALSE
1636 | Balasore | TOBV-05_HDR-TOBV-BIOHSD | HDR-TOBV-BIOHSD | TOBV-05 | MOV.TOBV-05.OPEN_STATUS | TRUE | MOV.TOBV-05.REMOTE_STATUS | TRUE | MOV.TOBV-05.MAINTENANCE_STATUS | FALSE

## Tank Maintenance
SAPID | Location | Device Name | Tank ID | Tank Type | Product | TANK MAINTENANCE | Normal value | LEVEL SWITCH MAINTENANCE | Normal Value | Sensor_Id | Sensor_Type | RADAR MAINTENANCE | Normal value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | ROSOV MAINTENANCE IL2 | Normal Value | Sensor_id | Sensor_type | ROSOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | ROSOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_type | MOV MAINTENANCE IL1 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE IL2 | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE RCL | Normal Value | Sensor_Id | Sensor_Type | MOV MAINTENANCE OL | Normal Value | Sensor_id | Sensor_Type | RIM SEAL MAINTENANCE STATUS | Normal Value
1636 | Balasore_M | TK-01_BS VI HSD | TK-01 | AG | BS VI HSD | TANK.TK-01.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-01.MAINTENANCE_STATUS | 0 | LSW-01 | VFT | LEVELSWITCH.RDR-01.MAINTENANCE_STATUS | 0 | RDR-01 | RADAR | MOV.ROSOV-03.MAINTENANCE_STATUS | 0 | ROSOV-03 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-02.MAINTENANCE_STATUS | 0 | ROSOV-02 | ROSOV OL | MOV.ROSOV-01.MAINTENANCE_STATUS | 0 | ROSOV-01 | ROSOV RCL | MOV.MOV-03.MAINTENANCE_STATUS | 0 | MOV-03 | MOV IL1 |  |  |  |  | MOV.MOV-02.MAINTENANCE_STATUS | 0 | MOV-02 | MOV RCL | MOV.MOV-01.MAINTENANCE_STATUS | 0 | MOV-01 | MOV OL
1636 | Balasore_M | TK-02_BS VI HSD | TK-02 | AG | BS VI HSD | TANK.TK-02.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-02.MAINTENANCE_STATUS | 0 | LSW-02 | VFT | LEVELSWITCH.RDR-02.MAINTENANCE_STATUS | 0 | RDR-02 | RADAR | MOV.ROSOV-06.MAINTENANCE_STATUS | 0 | ROSOV-06 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-05.MAINTENANCE_STATUS | 0 | ROSOV-05 | ROSOV OL | MOV.ROSOV-04.MAINTENANCE_STATUS | 0 | ROSOV-04 | ROSOV RCL | MOV.MOV-04.MAINTENANCE_STATUS | 0 | MOV-04 | MOV IL1 |  |  |  |  | MOV.MOV-06.MAINTENANCE_STATUS | 0 | MOV-06 | MOV RCL | MOV.MOV-05.MAINTENANCE_STATUS | 0 | MOV-05 | MOV OL
1636 | Balasore_M | TK-03_SKO | TK-03 | AG | SKO | TANK.TK-03.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-03.MAINTENANCE_STATUS | 0 | LSW-03 | VFT | LEVELSWITCH.RDR-03.MAINTENANCE_STATUS | 0 | RDR-03 | RADAR | MOV.ROSOV-09.MAINTENANCE_STATUS | 0 | ROSOV-09 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-08.MAINTENANCE_STATUS | 0 | ROSOV-08 | ROSOV OL | MOV.ROSOV-07.MAINTENANCE_STATUS | 0 | ROSOV-07 | ROSOV RCL | MOV.MOV-09.MAINTENANCE_STATUS | 0 | MOV-09 | MOV IL1 |  |  |  |  | MOV.MOV-07.MAINTENANCE_STATUS | 0 | MOV-07 | MOV RCL | MOV.MOV-08.MAINTENANCE_STATUS | 0 | MOV-08 | MOV OL
1636 | Balasore_M | TK-04_ETHANOL | TK-04 | AG | ETHANOL | TANK.TK-04.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-04.MAINTENANCE_STATUS | 0 | LSW-04 | VFT | LEVELSWITCH.RDR-04.MAINTENANCE_STATUS | 0 | RDR-04 | RADAR | MOV.ROSOV-12.MAINTENANCE_STATUS | 0 | ROSOV-12 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-11.MAINTENANCE_STATUS | 0 | ROSOV-11 | ROSOV OL | MOV.ROSOV-10.MAINTENANCE_STATUS | 0 | ROSOV-10 | ROSOV RCL | MOV.MOV-12.MAINTENANCE_STATUS | 0 | MOV-12 | MOV IL1 |  |  |  |  | MOV.MOV-10.MAINTENANCE_STATUS | 0 | MOV-10 | MOV RCL | MOV.MOV-11.MAINTENANCE_STATUS | 0 | MOV-11 | MOV OL
1636 | Balasore_M | TK-05_BS VI MS | TK-05 | AG | BS VI MS | TANK.TK-05.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-05.MAINTENANCE_STATUS | 0 | LSW-05 | VFT | LEVELSWITCH.RDR-05.MAINTENANCE_STATUS | 0 | RDR-05 | RADAR | MOV.ROSOV-15.MAINTENANCE_STATUS | 0 | ROSOV-15 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-13.MAINTENANCE_STATUS | 0 | ROSOV-13 | ROSOV OL | MOV.ROSOV-14.MAINTENANCE_STATUS | 0 | ROSOV-14 | ROSOV RCL | MOV.MOV-15.MAINTENANCE_STATUS | 0 | MOV-15 | MOV IL1 |  |  |  |  | MOV.MOV-14.MAINTENANCE_STATUS | 0 | MOV-14 | MOV RCL | MOV.MOV-13.MAINTENANCE_STATUS | 0 | MOV-13 | MOV OL
1636 | Balasore_M | TK-07_BS VI MS | TK-07 | AG | BS VI MS | TANK.TK-07.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-07.MAINTENANCE_STATUS | 0 | LSW-07 | VFT | LEVELSWITCH.RDR-07.MAINTENANCE_STATUS | 0 | RDR-07 | RADAR | MOV.ROSOV-16.MAINTENANCE_STATUS | 0 | ROSOV-16 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-17.MAINTENANCE_STATUS | 0 | ROSOV-17 | ROSOV OL | MOV.ROSOV-18.MAINTENANCE_STATUS | 0 | ROSOV-18 | ROSOV RCL | MOV.MOV-16.MAINTENANCE_STATUS | 0 | MOV-16 | MOV IL1 |  |  |  |  | MOV.MOV-18.MAINTENANCE_STATUS | 0 | MOV-18 | MOV RCL | MOV.MOV-17.MAINTENANCE_STATUS | 0 | MOV-17 | MOV OL
1636 | Balasore_M | TK-08_BS VI MS | TK-08 | UG | BS VI MS | TANK.TK-08.MAINTENANCE_STATUS | 0
1636 | Balasore_M | TK-09_ETHANOL | TK-09 | AG | ETHANOL | TANK.TK-09.MAINTENANCE_STATUS | 0
1636 | Balasore_M | TK-10_BS VI HSD | TK-10 | UG | BS VI HSD | TANK.TK-10.MAINTENANCE_STATUS | 0
1636 | Balasore_M | TK-13_BS VI HSD | TK-13 | AG | BS VI HSD | TANK.TK-13.MAINTENANCE_STATUS | 0
1636 | Balasore_M | TK-14_ETHANOL | TK-14 | AG | ETHANOL | TANK.TK-14.MAINTENANCE_STATUS | 0
1636 | Balasore_M | TK-15_ETHANOL | TK-15 | AG | ETHANOL | TANK.TK-15.MAINTENANCE_STATUS | 0 | LEVELSWITCH.LSW-06.MAINTENANCE_STATUS | 0 | LSW-06 | VFT | LEVELSWITCH.RDR-06.MAINTENANCE_STATUS | 0 | RDR-06 | RADAR | MOV.ROSOV-19.MAINTENANCE_STATUS | 0 | ROSOV-19 | ROSOV IL1 |  |  |  |  | MOV.ROSOV-20.MAINTENANCE_STATUS | 0 | ROSOV-20 | ROSOV OL | MOV.ROSOV-21.MAINTENANCE_STATUS | 0 | ROSOV-21 | ROSOV RCL | MOV.MOV-19.MAINTENANCE_STATUS | 0 | MOV-19 | MOV IL1 |  |  |  |  | MOV.MOV-21.MAINTENANCE_STATUS | 0 | MOV-21 | MOV RCL | MOV.MOV-20.MAINTENANCE_STATUS | 0 | MOV-20 | MOV OL

## Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction(Reciept/Dispatch) | PUMP ON STATUS | PUMP ON STATUS Normal value | PUMP LR STATUS | PUMP LR STATUS Normal value | PUMP MAINTENANCE STATUS | Normal Value
1636 | Balasore | ADTV PMP-1 BLUE DYE_BLUE DYE_DISPATCH | ADTV PMP-1 BLUE DYE | BLUE DYE | PUMP HOUSE | DISPATCH | PUMP.ADTV PMP-1 BLUE DYE.ON | 0 | PUMP.ADTV PMP-1 BLUE DYE.REMOTE_STATUS | 1 | PUMP.ADTV PMP-1 BLUE DYE.MAINTENANCE_STATUS | 0
1636 | Balasore | ADTV PMP-1 POWER_POWER_DISPATCH | ADTV PMP-1 POWER | POWER | PUMP HOUSE | DISPATCH | PUMP.ADTV PMP-1 POWER.ON | 0 | PUMP.ADTV PMP-1 POWER.REMOTE_STATUS | 1 | PUMP.ADTV PMP-1 POWER.MAINTENANCE_STATUS | 0
1636 | Balasore | ADTV PMP-1 TURBO_TURBO_DISPATCH | ADTV PMP-1 TURBO | TURBO | PUMP HOUSE | DISPATCH | PUMP.ADTV PMP-1 TURBO.ON | 0 | PUMP.ADTV PMP-1 TURBO.REMOTE_STATUS | 1 | PUMP.ADTV PMP-1 TURBO.MAINTENANCE_STATUS | 0
1636 | Balasore | ADTV PMP-2 BLUE DYE_BLUE DYE_DISPATCH | ADTV PMP-2 BLUE DYE | BLUE DYE | PUMP HOUSE | DISPATCH | PUMP.ADTV PMP-2 BLUE DYE.ON | 0 | PUMP.ADTV PMP-2 BLUE DYE.REMOTE_STATUS | 1 | PUMP.ADTV PMP-2 BLUE DYE.MAINTENANCE_STATUS | 0
1636 | Balasore | ADTV PMP-2 POWER_POWER_DISPATCH | ADTV PMP-2 POWER | POWER | PUMP HOUSE | DISPATCH | PUMP.ADTV PMP-2 POWER.ON | 0 | PUMP.ADTV PMP-2 POWER.REMOTE_STATUS | 1 | PUMP.ADTV PMP-2 POWER.MAINTENANCE_STATUS | 0
1636 | Balasore | ADTV PMP-2 TURBO_TURBO_DISPATCH | ADTV PMP-2 TURBO | TURBO | PUMP HOUSE | DISPATCH | PUMP.ADTV PMP-2 TURBO.ON | 0 | PUMP.ADTV PMP-2 TURBO.REMOTE_STATUS | 1 | PUMP.ADTV PMP-2 TURBO.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-01_BS VI MS_DISPATCH | PMP-01 | BS VI MS | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-01.ON | 0 | PUMP.PMP-01.REMOTE_STATUS | 1 | PUMP.PMP-01.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-02_BS VI MS_DISPATCH | PMP-02 | BS VI MS | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-02.ON | 0 | PUMP.PMP-02.REMOTE_STATUS | 1 | PUMP.PMP-02.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-03_BS VI HSD_DISPATCH | PMP-03 | BS VI HSD | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-03.ON | 0 | PUMP.PMP-03.REMOTE_STATUS | 1 | PUMP.PMP-03.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-04_BS VI HSD_DISPATCH | PMP-04 | BS VI HSD | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-04.ON | 0 | PUMP.PMP-04.REMOTE_STATUS | 1 | PUMP.PMP-04.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-05_SKO_DISPATCH | PMP-05 | SKO | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-05.ON | 0 | PUMP.PMP-05.REMOTE_STATUS | 1 | PUMP.PMP-05.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-06_SKO_DISPATCH | PMP-06 | SKO | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-06.ON | 0 | PUMP.PMP-06.REMOTE_STATUS | 1 | PUMP.PMP-06.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-07_ETHANOL_DISPATCH | PMP-07 | ETHANOL | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-07.ON | 0 | PUMP.PMP-07.REMOTE_STATUS | 1 | PUMP.PMP-07.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-08_ETHANOL_DISPATCH | PMP-08 | ETHANOL | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-08.ON | 0 | PUMP.PMP-08.REMOTE_STATUS | 1 | PUMP.PMP-08.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-10_BS VI MS_DISPATCH | PMP-10 | BS VI MS | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-10.ON | 0 | PUMP.PMP-10.REMOTE_STATUS | 1 | PUMP.PMP-10.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-11_BS VI HSD_DISPATCH | PMP-11 | BS VI HSD | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-11.ON | 0 | PUMP.PMP-11.REMOTE_STATUS | 1 | PUMP.PMP-11.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-12_BS VI HSD_DISPATCH | PMP-12 | BS VI HSD | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-12.ON | 0 | PUMP.PMP-12.REMOTE_STATUS | 1 | PUMP.PMP-12.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-13_SKO_DISPATCH | PMP-13 | SKO | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-13.ON | 0 | PUMP.PMP-13.REMOTE_STATUS | 1 | PUMP.PMP-13.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-14_SKO_DISPATCH | PMP-14 | SKO | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-14.ON | 0 | PUMP.PMP-14.REMOTE_STATUS | 1 | PUMP.PMP-14.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-15_ETHANOL_DISPATCH | PMP-15 | ETHANOL | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-15.ON | 0 | PUMP.PMP-15.REMOTE_STATUS | 1 | PUMP.PMP-15.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-16_ETHANOL_DISPATCH | PMP-16 | ETHANOL | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-16.ON | 0 | PUMP.PMP-16.REMOTE_STATUS | 1 | PUMP.PMP-16.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-17_ETHANOL_DISPATCH | PMP-17 | ETHANOL | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-17.ON | 0 | PUMP.PMP-17.REMOTE_STATUS | 1 | PUMP.PMP-17.MAINTENANCE_STATUS | 0
1636 | Balasore | PMP-18_ETHANOL_DISPATCH | PMP-18 | ETHANOL | TTL PUMP HOUSE | DISPATCH | PUMP.PMP-18.ON | 0 | PUMP.PMP-18.REMOTE_STATUS | 1 | PUMP.PMP-18.MAINTENANCE_STATUS | 0
1636 | Balasore | TWL-01_BS VI HSD_RECEIPT | TWL-01 | BS VI HSD | TWD PUMP HOUSE | RECEIPT | PUMP.TWL-01.ON | 0 | PUMP.TWL-01.REMOTE_STATUS | 1 | PUMP.TWL-01.MAINTENANCE_STATUS | 0
1636 | Balasore | TWL-02_BS VI HSD_RECEIPT | TWL-02 | BS VI HSD | TWD PUMP HOUSE | RECEIPT | PUMP.TWL-02.ON | 0 | PUMP.TWL-02.REMOTE_STATUS | 1 | PUMP.TWL-02.MAINTENANCE_STATUS | 0
1636 | Balasore | TWL-03_BS VI MS_RECEIPT | TWL-03 | BS VI MS | TWD PUMP HOUSE | RECEIPT | PUMP.TWL-03.ON | 0 | PUMP.TWL-03.REMOTE_STATUS | 1 | PUMP.TWL-03.MAINTENANCE_STATUS | 0
1636 | Balasore | TWL-04_BS VI MS_RECEIPT | TWL-04 | BS VI MS | TWD PUMP HOUSE | RECEIPT | PUMP.TWL-04.ON | 0 | PUMP.TWL-04.REMOTE_STATUS | 1 | PUMP.TWL-04.MAINTENANCE_STATUS | 0
1636 | Balasore | TWL-05_SKO_RECEIPT | TWL-05 | SKO | TWD PUMP HOUSE | RECEIPT | PUMP.TWL-05.ON | 0 | PUMP.TWL-05.REMOTE_STATUS | 1 | PUMP.TWL-05.MAINTENANCE_STATUS | 0
1636 | Balasore | TWL-06_SKO_RECEIPT | TWL-06 | SKO | TWD PUMP HOUSE | RECEIPT | PUMP.TWL-06.ON | 0 | PUMP.TWL-06.REMOTE_STATUS | 1 | PUMP.TWL-06.MAINTENANCE_STATUS | 0

## Fire Pump Master
SAPID | Location | Device Name | Pump ID | Fuel Type | Pump Type | Pump Direction | PUMP ON STATUS | Normal value | PUMP LR STATUS | Normal value | FIRE PUMP MAINTENANCE | Normal value | FIRE PUMP FAIL TO START 1 | Normal value | FIRE PUMP FAIL TO START 2 | Normal value | FIRE PUMP FAIL TO START 3 | Normal value | FIRE PUMP FAIL TO START STANDBY | Normal value | FIRE PUMP TRIPPED FAULT | Normal value | FIRE PUMP LLOP ALARM | Normal value | FIRE PUMP HWT ALARM | Normal value
1636 | Balasore | FWP-01_Water_DISPATCH | FWP-01 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-01.ON | 0 | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-01.MAINTENANCE_STATUS | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-01.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-01.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-01.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-01.HIGH_TEMPERATURE_ALARM | 0
1636 | Balasore | FWP-02_Water_DISPATCH | FWP-02 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-02.ON | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-02.MAINTENANCE_STATUS | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-02.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-02.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-02.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-02.HIGH_TEMPERATURE_ALARM | 0
1636 | Balasore | FWP-03_Water_DISPATCH | FWP-03 | Water | PUMP HOUSE | DISPATCH | PUMP.FWP-03.ON | 0 | PUMP.FWP-03.REMOTE_STATUS | 0 | PUMP.FWP-03.MAINTENANCE_STATUS | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN1 | 0 | PUMP.FWP-03.FAILED_TO_START_MAIN2 | 0 |  |  | PUMP.FWP-03.FAILED_TO_START_STANDBY | 0 | PUMP.FWP-03.PUMP_TRIPPED | 0 |  |  | PUMP.FWP-03.HIGH_TEMPERATURE_ALARM | 0
1636 | Balasore | JCY-01_Jockey_DISPATCH | JCY-01 | Jockey | PUMP HOUSE | DISPATCH | PUMP.JCY-01.ON | 0 | PUMP.JCY-01.REMOTE_STATUS | 0 | PUMP.JCY-01.MAINTENANCE_STATUS | 0 | PUMP.JCY-01.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-01.FAILED_TO_START_STANDBY | 0
1636 | Balasore | JCY-02_Jockey_DISPATCH | JCY-02 | Jockey | PUMP HOUSE | DISPATCH | PUMP.JCY-02.ON | 0 | PUMP.JCY-02.REMOTE_STATUS | 0 | PUMP.JCY-02.MAINTENANCE_STATUS | 0 | PUMP.JCY-02.FAILED_TO_START_MAIN1 | 0 |  |  |  |  | PUMP.JCY-02.FAILED_TO_START_STANDBY | 0
1636 | Balasore | Farthest Point PT_WP_DISPATCH | Farthest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-01.MAINTENANCE_STATUS
1636 | Balasore | Nearest Point PT_WP_DISPATCH | Nearest Point PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-02.MAINTENANCE_STATUS
1636 | Balasore | Farthest PT_WP_DISPATCH | Farthest PT | WP | PT | DISPATCH |  |  |  |  | PressureTransmitter.PT-03.MAINTENANCE_STATUS

## UPS Master
SAPID | Location | Device Name | UPS ID | Location | UPS FAIL | Normal Value | LOW BATTERY | Normal Value | UPS ON | Normal Value | UPS MAIN AC FAIL | Normal Value
1636 | Balasore | UPS-01_Control Room | UPS-01 | Control Room |  |  | UPS.UPS-01.LOW_BATTERY | 0 | UPS.UPS-01.LOAD_ON_UPS | 0 | UPS.UPS-01.MAIN_AC_FAIL | 0
1636 | Balasore | UPS-02_Control Room | UPS-02 | Control Room |  |  | UPS.UPS-02.LOW_BATTERY | 0 | UPS.UPS-02.LOAD_ON_UPS | 0 | UPS.UPS-02.MAIN_AC_FAIL | 0
1636 | Balasore | UPS-03_Control Room | UPS-03 | Control Room |  |  | UPS.UPS-03.LOW_BATTERY | 0 | UPS.UPS-03.UPS_ON | 0 | UPS.UPS-03.MAIN_AC_FAIL | 0
1636 | Balasore | UPS-04_Control Room | UPS-04 | Control Room |  |  | UPS.UPS-04.LOW_BATTERY | 0 | UPS.UPS-04.UPS_ON | 0 | UPS.UPS-04.MAIN_AC_FAIL | 0

## PLC Master
SAPID | Location | Device Name | PLC ID | Location | PLC A IS MASTER | Normal Value | Sensor_Id | Sensor_type | PLC B IS MASTER | Normal Value | Sensor_Id | Sensor_Type | PLC A FAIL SAFE | Normal Value | Sensor_id | Sensor_Type | PLC B FAIL SAFE | Normal Value | Sensor_Id | Senosr_Type | PLC A COOMUNCIATION | Normal Value | Sensor_id | Sensor_Type | PLC B COOMUNCIATION | Normal Value | Sensor_Id | Sensor_Type
1636 | Balasore | GEPLC_Process PLC | GEPLC | Process PLC | PLC.TASPLC.PLCA_IS_MASTER | 1 | TASPLC | PLCA | PLC.TASPLC.PLCB_IS_MASTER | 1 | TASPLC | PLCB
1636 | Balasore | SFT PLC_Safety PLC | SFT PLC | Safety PLC | PLC.SFTPLC.PLCA_IS_MASTER | 1 | SFTPLC | PLCA | PLC.SFTPLC.PLCB_IS_MASTER | 1 | SFTPLC | PLCB

## HCD Master
SAPID | Location | Device Name | HCD ID | Type | Location | HCD 40 % ALARM | Normal Value | HCD 20 % ALARM | Normal Value | HCD FAULT | Normal Value | MISALIGNMENT FAULT | Normal Value | HCD MAINTENANCE | Normal Value | HCD Hooter Activated | Normal value
1636 | Balasore | HDS-01_OPEN TYPE_TANK 05 | HDS-01 | OPEN TYPE | TANK 05 | GDS.HDS-01.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-01.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-01.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-01.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-01.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-02_OPEN TYPE_TLF PUMP HOUSE | HDS-02 | OPEN TYPE | TLF PUMP HOUSE | GDS.HDS-02.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-02.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-02.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-02.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-02.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-03_OPEN TYPE_TWD PUMP HOUSE | HDS-03 | OPEN TYPE | TWD PUMP HOUSE | GDS.HDS-03.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-03.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-03.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-03.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-03.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-04_FIXED TYPE_TANK 06 FIXED | HDS-04 | FIXED TYPE | TANK 06 FIXED | GDS.HDS-04.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-04.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-04.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-04.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-04.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-05_OPEN TYPE_TANK 07 OPEN | HDS-05 | OPEN TYPE | TANK 07 OPEN | GDS.HDS-05.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-05.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-05.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-05.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-05.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-07_FIXED TYPE_NR TK-05 FIXED | HDS-07 | FIXED TYPE | NR TK-05 FIXED | GDS.HDS-07.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-07.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-07.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-07.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-07.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-08_OPEN TYPE_NR TK-06 OPEN | HDS-08 | OPEN TYPE | NR TK-06 OPEN | GDS.HDS-08.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-08.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-08.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-08.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-08.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | HDS-09_FIXED TYPE_NR TLF PH FIXED TYPE | HDS-09 | FIXED TYPE | NR TLF PH FIXED TYPE | GDS.HDS-09.HYDROCARBON_40_PCT_LEL | 0 | GDS.HDS-09.HYDROCARBON_20_PCT_LEL | 0 | GDS.HDS-09.CRITICAL_FAULT_ALARM | 0 | GDS.HDS-09.MISALIGNMENT_FAULT_ALARM | 0 | GDS.HDS-09.MAINTENANCE_CALL | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Dyke Master
SAPID | Location | Dyke ID | DYKE VALVE STATUS | Normal Value | Dyke Hooter Activated | Normal value
1636 | Balasore | DV-01 | DRAINVALVE.DV-01.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | DV-02 | DRAINVALVE.DV-02.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0
1636 | Balasore | DV-03 | DRAINVALVE.DV-03.DRAIN_VALVE_STATUS | 0 | PLC.SFTPLC.HOOTER_FOR_HC_CR | 0

## Barrier Gate
SAPID | Location | Barrier ID | BARRIER GATE OPEN STATUS | Normal value | BARRIER GATE LR STATUS | Normal value
1636 | Balasore | EntryGate | GATE.EntryGate.OPEN_STATUS | 0 | GATE.EntryGate.REMOTE_STATUS | 1
1636 | Balasore | ExitGate | GATE.ExitGate.OPEN_STATUS | 0 | GATE.ExitGate.REMOTE_STATUS | 1

## Hooter Master
SAPID | Location | Device Name | Hooter ID | Hooter Name | HOOTER STATUS | Normal Value
1636 | Balasore | Hooter1_ANY_HOOTER_FOR_HCD_FIELD | Hooter1 | ANY_HOOTER_FOR_HCD_FIELD | PLC.SFTPLC.ANY_HOOTER_FOR_HCD_FIELD | 0
1636 | Balasore | Hooter2_HOOTER_FIELD_1 | Hooter2 | HOOTER_FIELD_1 | PLC.SFTPLC.HOOTER_FIELD_1 | 0
1636 | Balasore | Hooter3_HOOTER_FIELD_2 | Hooter3 | HOOTER_FIELD_2 | PLC.SFTPLC.HOOTER_FIELD_2 | 0
1636 | Balasore | Hooter4_HOOTER_FIELD_3 | Hooter4 | HOOTER_FIELD_3 | PLC.SFTPLC.HOOTER_FIELD_3 | 0
1636 | Balasore | Hooter5_HOOTER_FIELD_4 | Hooter5 | HOOTER_FIELD_4 | PLC.SFTPLC.HOOTER_FIELD_4 | 0

## ESD Master
SAPID | Location | Device Name | ESD ID | ESD Name | Location | ESD STATUS | Normal Value | ESD MAINTENANCE STATUS | Normal Value | All ROSOVs closed | Normal Value | Barrier Gate opened | Normal Value | TLF Gantry Permissive Power Off | Normal Value | All TLF Product Pumps Stopped | Normal Value | All Tanks in Dormant Mode | Normal Value | All DBBVs Closed | Normal Value | ESD Command To Process PLC | Normal Value | Siren Activated | Normal Value | ESD Hooter activated in control room | Normal Value | Power ESD Activation after 120 Sec | Normal Value | TTL Dispatch in Dormant Mode | Normal Value
1636 | Balasore | CENTRAL-ESD_CONTROL-ROOM | CENTRAL-ESD | ESD-CENTRAL | CONTROL-ROOM | ESD.CENTRAL-ESD.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-01_ESD-01-TM ROOM | ESD-PB-01 | ESD-PB-01 | ESD-01-TM ROOM | ESD.ESD-PB-01.ESD_STATUS | 0 | ESD.ESD-PB-01.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-02_ESD-02-Security Room | ESD-PB-02 | ESD-PB-02 | ESD-02-Security Room | ESD.ESD-PB-02.ESD_STATUS | 0 | ESD.ESD-PB-02.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-03_ESD-03-TLF ESD | ESD-PB-03 | ESD-PB-03 | ESD-03-TLF ESD | ESD.ESD-PB-03.ESD_STATUS | 0 | ESD.ESD-PB-03.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-04_ESD-04-TLF Gantry | ESD-PB-04 | ESD-PB-04 | ESD-04-TLF Gantry | ESD.ESD-PB-04.ESD_STATUS | 0 | ESD.ESD-PB-04.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-05_ESD-05-Outside Admin Block | ESD-PB-05 | ESD-PB-05 | ESD-05-Outside Admin Block | ESD.ESD-PB-05.ESD_STATUS | 0 | ESD.ESD-PB-05.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-06_ESD-06-Near Tank No 5 | ESD-PB-06 | ESD-PB-06 | ESD-06-Near Tank No 5 | ESD.ESD-PB-06.ESD_STATUS | 0 | ESD.ESD-PB-06.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-07_ESD-07-Near Tank No 6 & 7 | ESD-PB-07 | ESD-PB-07 | ESD-07-Near Tank No 6 & 7 | ESD.ESD-PB-07.ESD_STATUS | 0 | ESD.ESD-PB-07.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-08_ESD-08-Wagon Pump House | ESD-PB-08 | ESD-PB-08 | ESD-08-Wagon Pump House | ESD.ESD-PB-08.ESD_STATUS | 0 | ESD.ESD-PB-08.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-09_ESD-09-Near Tank No 1 & 4 | ESD-PB-09 | ESD-PB-09 | ESD-09-Near Tank No 1 & 4 | ESD.ESD-PB-09.ESD_STATUS | 0 | ESD.ESD-PB-09.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-10_ESD-10-Near Tank No 1 & 2 | ESD-PB-10 | ESD-PB-10 | ESD-10-Near Tank No 1 & 2 | ESD.ESD-PB-10.ESD_STATUS | 0 | ESD.ESD-PB-10.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-11_ESD-11-TTL Pump House | ESD-PB-11 | ESD-PB-11 | ESD-11-TTL Pump House | ESD.ESD-PB-11.ESD_STATUS | 0 | ESD.ESD-PB-11.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-PB-12_ESD-12-Railway Siding | ESD-PB-12 | ESD-PB-12 | ESD-12-Railway Siding | ESD.ESD-PB-12.ESD_STATUS | 0 | ESD.ESD-PB-12.MAINTENANCE_STATUS | 0 | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0
1636 | Balasore | ESD-SOFT_SOFT FROM OIC | ESD-SOFT | SOFT-ESD | SOFT FROM OIC | ESD.ESD-SOFT.ESD_STATUS | 0 |  |  | PLC.SFTPLC.ALL_ROSOV_CLOSED | 0 | PLC.SFTPLC.GATE_BARRIER_OPENED | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 | PLC.SFTPLC.ALL_TANKS_IN_DORMANT | 0 | PLC.SFTPLC.ALL_MOV_CLOSED | 0 | PLC.SFTPLC.ESD_STATUS_TO_PROCESS_PLC | 0 | PLC.SFTPLC.SIREN_ACTIVATED | 0 | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0 | PLC.SFTPLC.ESD_RELAY_PCC_PANEL | 0 | PLC.SFTPLC.ALL_DISPATCH_TANKS_IN_DORMANT | 0

## Loading Point Master
SAPID | Location | Device Name | Loading Point ID | Loading Point Type(TLF/TWF/TLFG/TWD) | BCU Number | Product | LP Earthing STATUS | Normal value | NO FLOW STATUS OF MAIN | Normal value | NO FLOW STATUS OF BLEND | Normal value | LOW FLOW STATUS OF MAIN | Normal value | LOW FLOW STATUS OF BLEND | Normal value | HIGH FLOW STATUS OF MAIN | Normal value | HIGH FLOW STATUS OF BLEND | Normal value | UNAUTHORISE FLOW STATUS OF MAIN | Normal value | METER OVERRUN STATUS OF MAIN | Normal value | BLEND OVERDOSE STATUS OF MAIN | Normal value | BLEND UNDERDOSE STATUS OF MAIN | Normal value | ADD OVERDOSE STATUS OF MAIN | Normal value | ADD UNDERDOSE STATUS OF MAIN | Normal value | BCU LOADING STATUS | Normal value | K-FACTOR CHANGE STATUS | Normal value | K-FACTOR CHANGE STATUS BLEND | Normal value | BCU VS MFM TOTALIZER MISMATCH | Normal Value | DAY START TOTALIZER MISMATCH | Normal value | DAY START TOTALIZER MISMATCH BLEND | Normal value
1636 | Balasore | LP 01_BC-01A_BS VI MS | LP 01 | TLF | BC-01A | BS VI MS | SmartLoad-Dual.BC-01A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-01A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-01A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-01A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 02_BC-01B_BS VI HSD | LP 02 | TLF | BC-01B | BS VI HSD | SmartLoad-Dual.BC-01B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-01B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-01B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-01B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-01B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-01B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-01B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 03_BC-02A_BS VI MS | LP 03 | TLF | BC-02A | BS VI MS | SmartLoad-Dual.BC-02A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-02A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-02A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-02A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 04_BC-02B_BS VI HSD | LP 04 | TLF | BC-02B | BS VI HSD | SmartLoad-Dual.BC-02B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-02B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-02B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-02B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-02B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-02B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-02B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 05_BC-03A_BS VI MS | LP 05 | TLF | BC-03A | BS VI MS | SmartLoad-Dual.BC-03A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-03A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-03A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-03A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 06_BC-03B_BS VI HSD | LP 06 | TLF | BC-03B | BS VI HSD | SmartLoad-Dual.BC-03B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-03B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-03B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-03B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-03B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-03B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-03B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 07_BC-04A_BS VI MS | LP 07 | TLF | BC-04A | BS VI MS | SmartLoad-Dual.BC-04A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.NO_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.LOW_FLOW_ALARM_STATUS_M2 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.HIGH_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-04A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.NOMINAL_ARM1_COMP2_KFACTOR_CHANGED | 0 | SmartLoad-Dual.BC-04A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0 | SmartLoad-Dual.BC-04A.BCU_C2_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 08_BC-04B_BS VI HSD | LP 08 | TLF | BC-04B | BS VI HSD | SmartLoad-Dual.BC-04B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-04B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-04B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-04B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-04B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-04B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-04B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 09_BC-05A_SKO | LP 09 | TLF | BC-05A | SKO | SmartLoad-Dual.BC-05A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-05A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-05A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-05A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 10_BC-05B_BS VI HSD | LP 10 | TLF | BC-05B | BS VI HSD | SmartLoad-Dual.BC-05B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-05B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-05B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-05B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-05B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-05B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-05B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 11_BC-06A_SKO | LP 11 | TLF | BC-06A | SKO | SmartLoad-Dual.BC-06A.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.NO_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-06A.LOW_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-06A.HIGH_FLOW_ALARM_STATUS_M1 | 0 |  |  | SmartLoad-Dual.BC-06A.UNAUTHORIZE_FLOW_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.METER_OVERRUN_ALARM_STATUS_M1 | 0 | SmartLoad-Dual.BC-06A.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06A.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06A.NOMINAL_ARM1_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-06A.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06A.BCU_C1_TOTALIZER_MISMATCH_ALARM | 0
1636 | Balasore | LP 12_BC-06B_BS VI HSD | LP 12 | TLF | BC-06B | BS VI HSD | SmartLoad-Dual.BC-06B.EARTH_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.NO_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.LOW_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.HIGH_FLOW_ALARM_STATUS_M3 | 0 |  |  | SmartLoad-Dual.BC-06B.UNAUTHORIZE_FLOW_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.METER_OVERRUN_ALARM_STATUS_M3 | 0 | SmartLoad-Dual.BC-06B.BLEND_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BLEND_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_OVERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.ADDITIVE_UNDERDOSE_ALARM_STATUS | 0 | SmartLoad-Dual.BC-06B.BATCH_STATUS | 0 | SmartLoad-Dual.BC-06B.NOMINAL_ARM2_COMP1_KFACTOR_CHANGED | 0 |  |  | SmartLoad-Dual.BC-06B.MFM_BCU_QTY_BEYOND_TOLERANCE_LIMIT_STATUS | 0 | SmartLoad-Dual.BC-06B.BCU_C3_TOTALIZER_MISMATCH_ALARM | 0

## Gantry override
SAPID | Location | Permissive override ID | OVERRIDE STATUS | Normal value
1636 | Balasore | Gantry Permissive override | PLC.SFTPLC.RESET_GANTRY_OPERATION | 0
1636 | Balasore | Gantry Permissive Write CMD status | SmartLoad-Dual.BC-01A.PERMISSIVE_FROM_DNC_STATUS | 0
1636 | Balasore | ESD Write CMD status | PLC.SFTPLC.ESD_FROM_DNC_STATUS | 0

## Fire Effect
SAPID | Location | Cause ID | Cause | Cause Normal value | TLF Gantry Permissive Power Off | Normal value | All TLF Product Pumps Stopped | Normal value | TLF Header Line MOV Close | Normal value | Hooter activated in control room | Normal value
1636 | Balasore | Two Fire Engine Running status | PLC.SFTPLC.FEP_2_RUNNING_STATUS | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1636 | Balasore | WATER Level below Ref. Volume | PLC.SFTPLC.WATERTK_VOL_BELOW_REF_VOL | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1636 | Balasore | Main Fire Engines not in REMOTE | PLC.SFTPLC.MAINS_FWP_IN_REMOTE | 0 | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0 | PLC.SFTPLC.ALL_TLF_PUMP_STOPPED | 0 |  |  | PLC.SFTPLC.HOOTER_FOR_ESD_CR | 0
1636 | Balasore | Gantry Permissive Off |  |  | PLC.SFTPLC.TLF_GANTRY_POWER_OFF | 0

## Air Compressor
SAPID | Location | Air Compressor ID | AIR COMPRESSOR FAULT STATUS | Normal value

## LRC Switchover
SAPID | Location | LRC ID | LRC SWITCHOVER 30 DAYS STATUS | Normal value
1636 | Balasore | LRC Switch Over | CLIENT.LRCA.HSB_COMMS_FAIL | 0

## OI
SAPID | Location | OI ID | Fire Engine1 | Normal Value | Fire Engine2 | Normal Value | Fire Engine3 | Normal Value | Jockey Pump Run1 | Normal Value | Jockey Pump Run2 | Normal Value | Farthest Point Pt | Normal value | Nearest Point PT | Normal value | Water Volume | Normal value | Main Fire Engine not in Remote | Normal value | Jockey Pump1 Remote | Normal value | Jockey Pump1 Auto | Normal value | Jockey Pump2 Remote | Normal value | Jockey Pump2 Auto | Normal value
1636 | Balasore | Operability Index | PUMP.FWP-01.REMOTE_STATUS | 0 | PUMP.FWP-02.REMOTE_STATUS | 0 | PUMP.FWP-03.REMOTE_STATUS | 0 | PUMP.JCY-01.ON | 0 | PUMP.JCY-02.ON | 0 | PressureTransmitter.PT-01.PRESSURE |  | PressureTransmitter.PT-02.PRESSURE |  | PLC.TASPLC.TOV_ON_SCREEN |  | PLC.SFTPLC.MAINS_FWP_IN_REMOTE | 0 | PUMP.JCY-01.REMOTE_STATUS | 1 | PUMP.JCY-01.AUTO_STATUS | 1 | PUMP.JCY-02.REMOTE_STATUS | 1 | PUMP.JCY-02.AUTO_STATUS | 1